## Instructions
AWWA Water Loss Control Committee (WLCC) Water Audit Software v3.0
PURPOSE: This spreadsheet-based water audit tool is designed to help quantify and track water losses associated with water distribution systems and identify areas for improved efficiency and cost recovery
USE: The spreadsheet contains several separate worksheets. Sheets can be accessed using the tabs towards the bottom of the screen, or by clicking the buttons on the left below. Descriptions of each sheet are also given below.
| THE FOLLOWING KEY APPLIES THROUGHOUT: |  |  | Value must be entered by user
Value may be entered by user
Value calculated based on input data
These cells contain recommended default values
Please begin by providing the following information, then proceed through each sheet in the workbook:
| NAME OF CITY OR UTILITY: |  |  |  | COUNTRY:
| REPORTING YEAR: |  | START DATE(MM/YYYY): |  | END DATE(MM/YYYY):
| NAME OF CONTACT PERSON: |  | E-MAIL: |  |  | TELEPHONE:
Ext.
PLEASE SELECT PREFERED REPORTING UNITS FOR WATER VOLUME:
| Click to advance to sheet… |  |  | Click here: for help about units and conversions
The current sheet
Enter the required data on this worksheet to calculate the water balance
The values entered in the Reporting Worksheet are used to populate the water balance
Use this sheet to understand terms used in the audit process
Use this sheet to help interpret the results of the performance indicators
[6 empty] | If you have questions or comments regarding the software please contact us at: | wlc@awwa.org
Instructions
Reporting Worksheet
Water Loss Standing
Water Balance
Definitions
Copyright © 2006, American Water Works Association. All Rights Reserved.
WASv3.0
?

## Reporting Worksheet
0
AWWA WLCC Water Audit Software: Reporting Worksheet
Water Audit Report for:
Reporting Year:
PLEASE CHOOSE REPORTING UNITS FROM THE INSTRUCTIONS SHEET BEFORE ENTERING DATA
WATER SUPPLIED
Volume from own sources:
Master meter error adjustment:
Water imported:
Water exported:
.
|  | WATER SUPPLIED: | . | 0
.
.
|  | AUTHORIZED CONSUMPTION | .
Billed metered:
Billed unmetered:
|  | Unbilled metered: |  |  |  | Pcnt: | Value:
|  | Unbilled unmetered: |  | 0 |  | 1.25% |  | 1
.
|  | AUTHORIZED CONSUMPTION: | . | 0
.
.
|  | WATER LOSSES (Water Supplied - Authorized Consumption) | . | 0
.
|  | Apparent Losses | . |  |  | Pcnt: | Value:
|  | Unauthorized consumption: |  | 0 |  | 0.25% |  | 1
|  | Customer metering inaccuracies: |  | 0 |  | 2% |  | 2
Systematic data handling errors:
|  | Apparent Losses: | . | 0
|  | Real Losses | .
|  | Real Losses = (Water Losses - Apparent Losses): | . | 0
.
|  | WATER LOSSES: | . | 0
.
.
|  | NON-REVENUE WATER | .
|  | NON-REVENUE WATER: | . | 0
.
|  | SYSTEM DATA | .
.
Length of mains:
Number of active AND inactive service connections:
|  | Connection density: | .
Average length of customer service line:
.
Average operating pressure:
.
|  | COST DATA | .
.
|  | Total annual cost of operating water system: |  |  | $/Year
Customer retail unit cost (applied to Apparent Losses):
|  | Variable production cost (applied to Real Losses): |  |  | $/
DATA REVIEW - Please review the following information and make changes above if necessary:
- Input values should be indicated as either measured or estimated. You have entered:
0 as measured values
0 as estimated values
2 as default values
16 without specifying measured, estimated or default
- Water Supplied Data: Volume of water imported is the same as the volume from own sources, please review and confirm
- Unbilled unmetered consumption: No problems identified
- Unauthorized consumption: No problems identified
- It is important to accurately measure the master meter - you have entered the measurement type as: unspecified
- Cost Data: None to evaluate
PERFORMANCE INDICATORS
Financial Indicators
Non-revenue water as percent by volume:
Non-revenue water as percent by cost:
Annual cost of Apparent Losses:
Annual cost of Real Losses:
Operational Efficiency Indicators
Apparent Losses per service connection per day:
Real Losses per service connection per day*:
Real Losses per length of main per day*:
Real Losses per service connection per day per meter (head) pressure:
Unavoidable Annual Real Losses (UARL):
Infrastructure Leakage Index (ILI) [Real Losses/UARL]:
* only the most applicable of these two indicators will be calculated
?
?
?
?
?
?
Click to access definition
?
?
?
?
?
?
Back to Instructions
Please enter data in the white cells below. Where possible, metered values should be used; if metered values are unavailable please estimate a value. Indicate this by selecting a choice from the gray box to the left, where M = measured (or accurately known value) and E = estimated.
?
?
?
?
?
?
?
?
?
(pipe length between curbstop and customer meter or property boundary)
Copyright © 2006, American Water Works Association. All Rights Reserved.
Use buttons to select percentage OR value
WASv3.0
?
Click here:
for help using option buttons below

## Water Balance
AWWA WLCC Water Audit Software: Water Balance |  |  |  | Water Audit Report For: | Report Yr:
| Water Exported |  |  | Billed Water Exported
0
|  |  | Billed Authorized Consumption | Billed Metered Consumption (inc. water exported) | Revenue Water
0
Own Sources |  | Authorized Consumption | 0 | Billed Unmetered Consumption | 0
(Adjusted for known errors) |  |  |  | 0
|  | 0 | Unbilled Authorized Consumption | Unbilled Metered Consumption | Non-Revenue Water (NRW)
0
0 |  |  | 0 | Unbilled Unmetered Consumption
0
| Water Supplied |  |  | Unauthorized Consumption | 0
|  |  | Apparent Losses | 0
| 0 |  | 0 | Customer Metering Inaccuracies
0
Systematic Data Handling Errors
|  | Water Losses |  | 0
Water Imported |  | 0 |  | Leakage on Transmission and/or Distribution Mains
|  |  | Real Losses | Not broken down
0 |  |  | 0 | Leakage and Overflows at Utility's Storage Tanks
Not broken down
Leakage on Service Connections
Not broken down
Note on D7: The volume of metered and/or unmetered water taken by registered customers who are authorized to do so by the water supplier. This also includes water exported across operational boundaries. Authorized consumption may include items such as fire fighting, training, flushing of mains and sewers, street cleaning, public fountains and gardens etc. These may be billed, unbilled, metered or unmetered.
Note on D15: The difference between System Input volume and Authorized Consumption. Water losses can be considered as a total volume for the whole system, or for partial systems such as transmission or distribution schemes, or individual zones. Water losses consist of Real Losses and Apparent losses.
Note on E21: Physical water losses from a pressurized system and the utilities storage tanks up to the point of customer use. In metered systems this is the customer meter. In unmetered systems this is the first point of use (the stop tap or tap) within the property. This is the annual volume lost through all types of leaks, bursts and overflows.
Note on F7: All metered consumption which is billed. This includes all groups of customers such as domestic, commercial, industrial or institutional and also includes water transferred across operational boundaries (water exported) which is metered and billed.
Note on F9: All billed consumption which is calculated based on estimates or norms, but is not metered. This might be a small component in fully metered systems (for example billing based on estimates for the period a customer meter is out of order) but can be the key consumption component in systems without universal metering. This component may also include water transferred across operational boundaries (water exported) which is unmetered, but billed.
Note on F11: Metered consumption which is for any reason unbilled. This might for example include metered consumptionof the utility itself or water or water provided to institutions free of charge, including water transferred across operational boundaries (water exported) which is metered but unbilled.
Note on F13: Any kind of Authorized Consumption which is neither billed nor metered. This component typically includes items such as fire fighting, flushing of mains and sewers, street cleaning, frost protection, etc. In a well run utility it is a small component which is often substantially overestimated. Theoretically this might also include water transferred across operational boundaries (water exported) which is unmetered and unbilled, but this is unlikely.
Note on F15: Any unauthorized use of water. This may include illegal water use from hydrants (for example for construction purposes), illegal connections, bypasses to consumption meters or meter tampering.
Note on F17: Apparent water losses caused by customer meter inaccuracies.
Note on F19: Apparent water losses caused by data handling errors in the meter reading and billing system.
Note on F21: Physical water losses from a pressurized system up to the point of customer use. This is the annual volume lost through all types of leaks and bursts.
Note on F23: Physical water losses from the utility's storage tanks.
Note on F25: Physical water losses from the utility's service lines between the distribution main (corporation stop) and the point of customer use (stop tap).
Note on G11: Water which does not provide any revenue to the utility.
Note on G7: Water which provides revenue to the utility.
Note on E11: All consumption that is unbilled, but is still authorized by the utility.
Note on E7: All consumption that is billed and authorized by the utility. This may include both metered and unmetered consumption.
Note on B5: The volume of treated water input to that part of the water supply system to which the water balance relates. This can be from your own production facilities or bulk supplies from others.
Note on E15: Includes all types of inaccuracies associated with customer metereing as well as data handling errors (meter reading and billing), plus unauthorized consumption (theft or illegal use). Note that over-registration of customer meteres leads to under-estimation of Real Losses. Under-registration of customer meters leads to over-estimation of Real Losses.
Copyright © 2006, American Water Works Association. All Rights Reserved.
WASv3.0

## Definitions
AWWA WLCC Water Audit Software: Definitions
Item Name | Description
Volume from own sources | The volume of treated water input to system from own production facilities
Master meter error adjustment | An estimate or measure of the degree of any inaccuracy that exists in the master meters measuring the Volume from own sources. Please also indicate if this adjustment is because the master meters under-registered (did not capture all the flow) or over-registered (overstated the actual flow)
Water imported | Bulk water purchased to become part of the water supplied. Typically this is water purchased from a neighboring water utility or regional water authority. Be sure to account for any import meter inaccuracy in reporting this volume
Water exported | Bulk water sold and conveyed out of the water distribution system. Typically this is water sold to a neighboring water utility. Be sure to account for any export meter inaccuracy in reporting this volume
AUTHORIZED CONSUMPTION | = billed metered + billed unmetered + unbilled metered + unbilled unmetered The volume of metered and/or unmetered water taken by registered customers, the water supplier and others who are implicitly or explicitly authorized to do so by the water supplier, for residential, commercial and industrial purposes. This does NOT include water sold to neighboring utilities (water exported). Authorized consumption may include items such as fire fighting and training, flushing of mains and sewers, street cleaning, watering of municipal gardens, public fountains, frost protection, building water, etc. These may be billed or unbilled, metered or unmetered.
Billed Authorized Consumption | All consumption that is billed and authorized by the utility. This may include both metered and unmetered consumption. See "Authorized Consumption" for more information.
Unbilled Authorized Consumption | All consumption that is unbilled, but still authorized by the utility. See "Authorized Consumption" for more information.
Billed metered consumption | All metered consumption which is billed. This includes all groups of customers such as domestic, commercial, industrial or institutional. It does NOT include water sold to neighboring utilities (water exported) which is metered and billed. The metered consumption data can be taken directly from billing records for the water audit period. The accuracy of yearly metered consumption data can be refined by including an adjustment to account for customer meter reading lagtime, however additional analysis is necessary to determine the adjustment value, which may or may not be significant.
Billed unmetered consumption | All billed consumption which is calculated based on estimates or norms but is not metered. This might be a very small component in fully metered systems (for example billing based on estimates for the period a customer meter is out of order) but can be the key consumption component in systems without universal metering. It does NOT include water sold to neighboring utilities (water exported) which is unmetered but billed.
Unbilled metered consumption | Metered Consumption which is for any reason unbilled. This might for example include metered consumption of the utility itself or water provided to institutions free of charge. It does NOT include water sold to neighboring utilities (water exported) which is metered but unbilled.
Unbilled unmetered consumption | Any kind of Authorized Consumption which is neither billed nor metered. This component typically includes items such as fire fighting, flushing of mains and sewers, street cleaning, frost protection, etc. In most water utilities it is a small component which is very often substantially overestimated. It does NOT include water sold to neighboring utilities (water exported) which is unmetered and unbilled – an unlikely case. This component has many sub-components of water use which are often tedious to identify and quantify. Because of this, and the fact that it is usually a small portion of the water supplied, it is recommended that the auditor apply the default value of 1.25% of the volume from own sources. Select the default percentage to enter this value. If the water utility already has well validated data that gives a value substantially higher or lower than the default volume, then the auditor should enter their own volume. However the default approach is recommended for most water utilities. Note that a value of zero is not permitted, since all water utilities have some volume of water in this component occurring in their system.
WATER LOSSES | = apparent losses + real losses The difference between System Input and Authorized Consumption. Water losses can be considered as a total volume for the whole system, or for partial systems such as transmission or distribution systems, or individual zones. Water Losses consist of Real Losses and Apparent Losses.
Apparent Losses | = unauthorized consumption + meter under-registration + data handling errors Includes all types of inaccuracies associated with customer metering as well as data handling errors (meter reading and billing), plus unauthorized consumption (theft or illegal use). NOTE: Over-registration of customer meters, leads to under-estimation of Real Losses. Under-registration of customer meters, leads to over-estimation of Real Losses.
Unauthorized consumption | Includes water illegally withdrawn from hydrants, illegal connections, bypasses to consumption meter or meter reading equipment tampering. While this component has a direct impact on revenue, in most water utilities the volume is low and it is recommended that the auditor apply a default value of 0.25% of the volume from own sources. If the auditor has well validated data that indicates the volume from unauthorized consumption is substantially higher or lower than that generated by the default value then this value can be entered. However, for most water utilities it is recommended to apply the default value. Note that a value of zero will not be accepted since all water utilities have some volume of unauthorized consumption occurring in their system.
Customer metering inaccuracies | Apparent water losses caused by the collective under-registration of customer water meters. Many customer water meters will wear as large cumulative volumes of water are passed through them over time. This causes the meters to under-register. The auditor has two options for entering data for this component of the audit. The auditor can enter a percentage under-registration (typically an estimated value), this will apply the selected percentage to the two categories of metered consumption to determine the volume of water not recorded due to customer meter inaccuracy. Alternatively, if the auditor has substantial data from meter testing to arrive at their own volumes of such losses, this volume may be entered directly. Note that a value of zero will be accepted but an alert will appear asking if the customer population is unmetered. Since all metered systems have some degree of inaccuracy, then a positive value should be entered. A value of zero in this component is valid only if the water utility does not meter its customer population.
Systematic data handling errors | Apparent water losses caused by systematic data handling errors in the meter reading and billing system.
Real Losses | Physical water losses from the pressurized system and the utility’s storage tanks, up to the point of customer consumption. In metered systems this is the customer meter, in unmetered situations this is the first point of consumption (stop tap/tap) within the property. The annual volume lost through all types of leaks, breaks and overflows depends on frequencies, flow rates, and average duration of individual leaks, breaks and overflows.
NON-REVENUE WATER | = Apparent Losses + Real Losses + Unbilled Metered + Unbilled Unmetered Water which does not provide any revenue to the utility
Revenue Water | Water which is charged to customers to provide revenue to the utility.
Length of mains | Length of all pipelines (except service connections) in the system starting from the point of system input metering (for example at the outlet of the treatment plant). It is also recommended to include in this measure the total length of fire hydrant lead pipe. Hydrant lead pipe is the pipe branching from the water main to the fire hydrant. Fire hydrant leads are typically of a sufficiently large size that is more representative of a pipeline than a service connection. The average length of hydrant leads across the entire system can be assumed if not known, and multiplied by the number of fire hydrants in the system, which can also be assumed if not known. This value can then be added to the total pipeline length. Total length of mains can therefore be calculated as: Length of Mains, miles = (total pipeline length, miles) + [ {(average fire hydrant lead length, ft) x (number of fire hydrants)} / 5,280 ft/mile ] or Length of Mains, kilometres = (total pipeline length, kilometres) + [ {(average fire hydrant lead length, metres) x (number of fire hydrants)} / 1,000 metres/kilometre ]
Number of active AND inactive service connections | Number of service connections, main to curb stop. Please note that this includes the actual number of distinct piping connections whether active or inactive. This may differ substantially from the number of Customers (or number of accounts)
Connection density | =number of connections / length of mains
Average length of customer service line | This is entered for unmetered services and in cold or other areas where meters are installed inside homes and buildings. It is the length of customer service line either between the utility's service connection (often at the curbstop) and the meter, or to the building line (first point of customer consumption) if customers are unmetered. Note that the length of service connection between the main and customer service line is owned by the utility and its length and potential leakage is accounted for in the UARL formula by the number of service connections.
Average operating pressure | The average pressure may be approximated when compiling the preliminary water audit. Once routine water auditing has been established, a more accurate assessment of average pressure should be pursued. If the water utility infrastructure is recorded in a Geographical Information System (GIS) the average pressure at many locations in the distribution system can be readily obtained. If a GIS does not exist, a weighted average of pressure data can be calculated from water pressure measured at various fire hydrants scattered across the water distribution system.
Total annual cost of operating the water system | These costs include those for operations, maintenance and any annually incurred costs for long-term upkeep of the system, such as repayment of capital bonds for infrastructure expansion or improvement. Typical costs include employee salaries and benefits, materials, equipment, insurance, fees, administrative costs and all other costs that exist to sustain the drinking water supply. These costs should not include any costs to operate wastewater, biosolids or other systems outside of drinking water.
Customer retail unit cost | The Customer Retail Unit Cost represents the charge that customers pay for water service. This unit cost is applied to the components of apparent loss, since these losses represent water reaching customers but not (fully) paid for. It is important to compile these costs per the same unit cost basis as the volume measure included in the water audit. For example, if all water volumes are measured in million gallons, then the unit cost should be dollars per million gallon ($/mil gal). The software allows the user to select the units that are charged to customers (either $/1,000 gallons, $/hundred cubic feet or $/1,000 litres) and automatically converts these units to the units that appear in the "WATER SUPPLIED" box. Since most water utilities have a rate structure that includes a variety of different costs based upon class of customer, a weighted average of individual costs and number of customer accounts in each class can be calculated to determine a single composite cost that should be entered into this cell.
Variable production cost (applied to Real Losses) | The cost to produce and supply the next unit of water. (E.g., $/million gallons) This cost is determined by calculating the summed unit costs for ground and surface water treatment and all power used for pumping from the source to the customer. It should also include the unit cost of bulk water purchased as an import if applicable.
Unavoidable Annual Real Losses (UARL) | UARL (gallons/day)=(5.41Lm + 0.15Nc + 7.5Lp) xP, or UARL (litres/day)=(18.0Lm + 0.8Nc + 25.0Lp) xP where: Lm = length of mains, (miles or kilometres) Nc = number of service connections Lp = total length of private pipe, (miles or km) = Nc x average distance of private pipe
The UARL is a theoretical reference value representing the technical low limit of leakage that could be achieved if all of today's best technology could be successfully applied. It is a key variable in the calculation of the Infrastructure Leakage Index (ILI). It is not necessary that water utilities set this level as the target level of leakage, unless water is unusually expensive, scarce or both. NOTE: The UARL calculation has not yet been fully proven as effective for very small water distribution systems. If, (Lm x 32) + Nc < 3000 (gallons per day) or (Lm x 20) + Nc < 3000 (litres per day) then the calculated UARL value may not be valid. The software does not display a value of UARL or ILI if either of these conditions is true.
Infrastructure Leakage Index (ILI) | The ratio of the Current Annual Real Losses (Real Losses) to the Unavoidable Annual Real Losses (UARL). The ILI is a highly effective performance indicator for comparing (benchmarking) the performance of utilities in operational management of real losses.
Use of Option Buttons
Units and Conversions | The user may develop an audit based on one of three unit selections: 1) Million Gallons (US) 2) Megalitres (Thousand Cubic Metres) 3) Acre-feet Once this selection has been made in the instructions sheet, all calculations are made on the basis of the chosen units. Should the user wish to make additional conversions, a unit converter is provided below (use drop down menus to select units from the yellow unit boxes):
| Enter Units: | Convert From… |  | Converts to…..
| 1 | Million Gallons (US) | = | 1 | Million Gallons (US)
(conversion factor = 1)
Find
Find
Find
Find
Find
Find
Find
Find
Find
Find
Back to Instructions
Find
Find
Find
Find
Find
Find
Find
Find
Find
Find
Copyright © 2006, American Water Works Association. All Rights Reserved.
WASv3.0
Find
To use the percent value choose this button
To enter a value choose this button and enter the value in the cell to the right
NOTE: For unbilled unmetered consumption and unauthorized consumption, a recommended default value can be applied by selecting the Percent option. The default values are based on fixed percentages of water supplied and are recommended for use in this audit unless the auditor has well validated data for their system. Default values are shown by purple cells, as shown in the example above.
If a default value is selected, the user does not need to identify if an estimated or measured value has been used, the user should leave the drop-down box empty.
Find

## Water Loss Standing
AWWA WLCC Water Audit Software: Determining Water Loss Standing?
Once data has been entered into the Reporting Worksheet, the performance indcators are automatically calculated. How does a water utility operator know how well his or her system is performing? The AWWA Water Loss Control Committee provided the following table to assist water utilities is gauging an approximate Infrastructure Leakage Index (ILI) that is appropriate for their water system and local conditions. The lower the amount of leakage and real losses that exist in the system, then the lower the ILI value will be. Note: this table offers an approximate guideline for leakage reduction target-setting. The best means of setting such targets include performing an economic assessment of various loss control methods. However, this table is useful if such an assessment is not possible.
General Guidelines for Setting a Target ILI (without doing a full economic analysis of leakage control options)
| Target ILI Range | Financial Considerations | Operational Considerations | Water Resources Considerations
1 | 1.0 - 3.0 | Water resources are costly to develop or purchase; ability to increase revenues via water rates is greatly limited because of regulation or low ratepayer affordability. | Operating with system leakage above this level would require expansion of existing infrastructure and/or additional water resources to meet the demand. | Available resources are greatly limited and are very difficult and/or environmentally unsound to develop.
2 | >3.0 -5.0 | Water resources can be developed or purchased at reasonable expense; periodic water rate increases can be feasibly imposed and are tolerated by the customer population. | Existing water supply infrastructure capability is sufficient to meet long-term demand as long as reasonable leakage management controls are in place. | Water resources are believed to be sufficient to meet long-term needs, but demand management interventions (leakage management, water conservation) are included in the long-term planning.
3 | >5.0 - 8.0 | Cost to purchase or obtain/treat water is low, as are rates charged to customers. | Superior reliability, capacity and intregrity of the water supply infrastructure make it relatively immune to supply shortages. | Water resources are plentiful, reliable, and easily extracted.
| Greater than 8.0 | Although operational and financial considerations may allow a long-term ILI greater than 8.0, such a level of leakage is not an effective utilization of water as a resource. Setting a target level greater than 8.0 - other than as an incremental goal to a smaller long-term target - is discouraged.
4 | Less than 1.0 | If the calculated Infrastructure Leakage Index (ILI) value for your system is 1.0 or less, two possibilities exist. a) you are maintaining your leakage at low levels in a class with the top worldwide performers in leakage control. b) A portion of your data may be flawed, causing your losses to be greatly understated. This is likely if you calculate a low ILI value but do not employ extensive leakage control practices in your operations. In such cases it is beneficial to validate the data by performing field measurements to confirm the accuracy of production and customer meters, or to identify any other potential sources of error in the data.
AWWA Water Audit Software Version 3.0 Developed by the Water Loss Control Committee of the American Water Works Association April 2007
ACKNOWLEDGMENTS
| DEVELOPED BY: | ANDREW CHASTAIN-HOWLEY, Water Prospecting and Resource Consulting
ANDREW DAY, Water Prospecting and Resource Consulting
DAVID GOFF, P.E. Goff Water Audits & Engineering
GEORGE KUNKEL, P.E. Philadelphia Water Department
ALAIN LALONDE, Veritec Consulting
DAVID SAYERS, Delaware River Basin Commission
| REFERENCES: | - Alegre, H., Hirner, W., Baptista, J. and Parena, R. Performance Indicators for Water Supply Services. IWA Publishing ‘Manual of Best Practice’ Series, 2000. ISBN 1 900222 272
- Kunkel, G. et al, 2003. Water Loss Control Committee Report: Applying Worldwide Best Management Practices in Water Loss Control. Journal AWWA, 95:8:65
Back to Instructions
Copyright © 2006, American Water Works Association. All Rights Reserved.
WASv3.0

## Ex. Audit 1 (Million Gallons)
0
AWWA WLCC Water Audit Software: Reporting Worksheet
|  | Water Audit Report for: | Philadelphia Water Department
|  | Reporting Year: | 2006
All volumes to be entered as: MILLION GALLONS (US) PER YEAR
WATER SUPPLIED
|  | Volume from own sources: |  | M | 92931.5 | million gallons (US)/yr (MG/Yr)
|  | Master meter error adjustment: |  | E | 294.2 | over-registered |  | MG/Yr
|  | Water imported: |  |  |  | MG/Yr
|  | Water exported: |  | M | 6971.5 | MG/Yr
.
|  | WATER SUPPLIED: |  | . | 85665.8 | MG/Yr
.
.
|  | AUTHORIZED CONSUMPTION |  | .
|  | Billed metered: |  | M | 57633.5 | MG/Yr
|  | Billed unmetered: |  |  | 0 | MG/Yr
|  | Unbilled metered: |  | M | 0.3 | MG/Yr | Pcnt: |  | Value:
|  | Unbilled unmetered: |  |  | 892.5 | MG/Yr | 1.25% |  | 892.5 | 2
.
|  | AUTHORIZED CONSUMPTION: |  | . | 58526.3 | MG/Yr
.
.
|  | WATER LOSSES (Water Supplied - Authorized Consumption) |  | . | 27139.5 | MG/Yr
.
|  | Apparent Losses |  | . |  |  | Pcnt: |  | Value:
|  | Unauthorized consumption: |  |  | 1579 | MG/Yr | 0.25% |  | 1579 | 2
|  | Customer metering inaccuracies: |  | E | 114.6 | MG/Yr | 2.25% |  | 114.6 | 2
|  | Systematic data handling errors: |  | E | 3826.4 | MG/Yr
|  | Apparent Losses: |  | . | 5520 | MG/Yr
|  | Real Losses |  | .
|  | Real Losses = (Water Losses - Apparent Losses): |  | . | 21619.5 | MG/Yr
.
|  | WATER LOSSES: |  | . | 27139.5 | MG/Yr
.
.
|  | NON-REVENUE WATER |  | .
|  | NON-REVENUE WATER: |  | . | 28032.3 | MG/Yr
.
|  | SYSTEM DATA |  | .
.
|  | Length of mains: |  | M | 3084 | miles
|  | Number of active AND inactive service connections: |  | M | 551959
|  | Connection density: |  | . | 178.975 | conn./mile main
|  | Average length of customer service line: |  | E | 12 | ft
.
|  | Average operating pressure: |  | M | 55 | psi
.
|  | COST DATA |  | .
.
|  | Total annual cost of operating water system: |  | M | 190162000 | $/Year
|  | Customer retail unit cost (applied to Apparent Losses): |  | M | 4.5 | $/1000 gallons (US)
|  | Variable production cost (applied to Real Losses): |  | M | 160.48 | $/million gallons (US)
DATA REVIEW - Please review the following information and make changes above if necessary:
- Input values should be indicated as either measured or estimated. You have entered:
10 as measured values
6 as estimated values
0 as default values
2 without specifying measured, estimated or default
- Water Supplied Data: No problems identified
- Unbilled unmetered consumption: No problems identified
- Unauthorized consumption: No problems identified
- It is important to accurately measure the master meter - you have entered the measurement type as: measured
- Cost Data: No problems identified
PERFORMANCE INDICATORS
Financial Indicators
[5 empty] | Non-revenue water as percent by volume: | 32.72%
[5 empty] | Non-revenue water as percent by cost: | 14.96%
[5 empty] | Annual cost of Apparent losses: | 24840000
[5 empty] | Annual cost of Real Losses: | 3469497.36
Operational Efficiency Indicators
[5 empty] | Apparent Losses per service connection per day: | 27.3993 | gallons/connection/day
[5 empty] | Real Losses per service connection per day*: | 107.3114 | gallons/connection/day
[5 empty] | Real Losses per length of main per day*: | N/A
[5 empty] | Real Losses per service connection per day per psi pressure: | 1.9511 | gallons/connection/day/psi
[5 empty] | Unavoidable Annual Real Losses (UARL): | 2185.9001 | million gallons/year
|  | Infrastructure Leakage Index (ILI) [Real Losses/UARL]: |  |  |  | 9.8904
* only the most applicable of these two indicators will be calculated
?
?
?
?
?
?
Click to access definition
?
?
?
?
?
?
Back to Instructions
Please enter data in the white cells below. Where possible, metered values should be used; if metered values are unavailable please estimate a value. Indicate this by selecting a choice from the gray box to the left, where M = measured (or accurately known value) and E = estimated.
?
?
?
?
?
?
?
?
?
(pipe length between curbstop and customer meter or property boundary)
Copyright © 2006, American Water Works Association. All Rights Reserved.
Use buttons to select percentage OR value
WASv3.0
?
Click here:
for help using option buttons below

## Ex. Audit 2 (Megalitres)
0
AWWA WLCC Water Audit Software: Reporting Worksheet
|  | Water Audit Report for: | Regional Municipality of Peel
|  | Reporting Year: | 2005
All volumes to be entered as: MEGALITRES (THOUSAND CUBIC METRES) PER YEAR
WATER SUPPLIED
|  | Volume from own sources: |  | M | 191513 | Megalitres/yr (or ML/Yr)
|  | Master meter error adjustment: |  | E | 0 |  |  | ML/Yr
|  | Water imported: |  | M | 0 | ML/Yr
|  | Water exported: |  | M | 1748.7 | ML/Yr
.
|  | WATER SUPPLIED: |  | . | 189764.3 | ML/Yr
.
.
|  | AUTHORIZED CONSUMPTION |  | .
|  | Billed metered: |  | M | 173394 | ML/Yr
|  | Billed unmetered: |  | E | 152.6 | ML/Yr
|  | Unbilled metered: |  | M | 0 | ML/Yr | Pcnt: |  | Value:
|  | Unbilled unmetered: |  |  | 912.8 | ML/Yr | 1.25% |  | 912.8 | 2
.
|  | AUTHORIZED CONSUMPTION: |  | . | 174459.4 | ML/Yr
.
.
|  | WATER LOSSES (Water Supplied - Authorized Consumption) |  | . | 15304.9 | ML/Yr
.
|  | Apparent Losses |  | . |  |  | Pcnt: |  | Value:
|  | Unauthorized consumption: |  |  | 886.2 | ML/Yr | 0.25% |  | 886.2 | 2
|  | Customer metering inaccuracies: |  | E | 3538.6531 | ML/Yr | 2% |  |  | 1
|  | Systematic data handling errors: |  | E | 0 | ML/Yr
|  | Apparent Losses: |  | . | 4424.8531 | ML/Yr
|  | Real Losses |  | .
|  | Real Losses = (Water Losses - Apparent Losses): |  | . | 10880.0469 | ML/Yr
.
|  | WATER LOSSES: |  | . | 15304.9 | ML/Yr
.
.
|  | NON-REVENUE WATER |  | .
|  | NON-REVENUE WATER: |  | . | 16217.7 | ML/Yr
.
|  | SYSTEM DATA |  | .
.
|  | Length of mains: |  | M | 3852.12 | kilometers
|  | Number of active AND inactive service connections: |  | M | 267335
|  | Connection density: |  | . | 69.3994 | conn./km main
|  | Average length of customer service line: |  | E | 7.5 | metres
.
|  | Average operating pressure: |  | E | 54.9 | metres (head)
.
|  | COST DATA |  | .
.
|  | Total annual cost of operating water system: |  | E | 73000000 | $/Year
|  | Customer retail unit cost (applied to Apparent Losses): |  | M | 0.441 | $/1000 litres
|  | Variable production cost (applied to Real Losses): |  | M | 441 | $/Megalitre
DATA REVIEW - Please review the following information and make changes above if necessary:
- Input values should be indicated as either measured or estimated. You have entered:
9 as measured values
9 as estimated values
0 as default values
0 without specifying measured, estimated or default
- Water Supplied Data: No problems identified
- Unbilled unmetered consumption: No problems identified
- Unauthorized consumption: No problems identified
- It is important to accurately measure the master meter - you have entered the measurement type as: measured
- Cost Data: Retail costs are less than (or equal to) production costs; please review and correct if necessary
PERFORMANCE INDICATORS
Financial Indicators
[5 empty] | Non-revenue water as percent by volume: | 8.546%
[5 empty] | Non-revenue water as percent by cost: | 9.797%
[5 empty] | Annual cost of Apparent losses: | 1951360.2
[5 empty] | Annual cost of Real Losses: | 4798100.7
Operational Efficiency Indicators
[5 empty] | Apparent Losses per service connection per day: | 45.3472 | litres/connection/day
[5 empty] | Real Losses per service connection per day*: | 111.5019 | litres/connection/day
[5 empty] | Real Losses per length of main per day*: | N/A
[5 empty] | Real Losses per service connection per day per meter (head) pressure: | 2.031 | litres/connection/day/m
[5 empty] | Unavoidable Annual Real Losses (UARL): | 6679.4627 | cubic meters/year
|  | Infrastructure Leakage Index (ILI) [Real Losses/UARL]: |  |  |  | 1.6289
* only the most applicable of these two indicators will be calculated
?
?
?
?
?
?
Click to access definition
?
?
?
?
?
?
Back to Instructions
Please enter data in the white cells below. Where possible, metered values should be used; if metered values are unavailable please estimate a value. Indicate this by selecting a choice from the gray box to the left, where M = measured (or accurately known value) and E = estimated.
?
?
?
?
?
?
?
?
?
(pipe length between curbstop and customer meter or property boundary)
Copyright © 2006, American Water Works Association. All Rights Reserved.
Use buttons to select percentage OR value
WASv3.0
?
Click here:
for help using option buttons below

## Sheet1 (hidden)
| $/100 cubic feet (ccf) | $/1000 gallons (US) | $/1000 litres |  | Conversion table | [6 empty] | FROM: TO: | Million gallons (US) | Megalitres (thousand cubic metres) | Acre-feet
Million gallons (US) | 1336.8056 | 1000 | 3785.4118 |  | 7.4805 | gallons / cubic foot | converting FROM volume unit TO pricing UNITS |  |  |  |  | Million gallons (US) | 1 | 3.7854 | 3.0689
Megalitres (thousand cubic metres) | 353.1467 | 264.1721 | 1000 |  | 43560 | sq feet / acre | [5 empty] | Megalitres (thousand cubic metres) | 0.26417 | 1 | 0.81071
Acre-feet | 435.6 | 325.8514 | 1233.4818 |  | 3.7854 | litres / gallon | [5 empty] | Acre-feet | 0.32585 | 1.2335 | 1
[5 empty] | 0.26417 | gallons / litre
losses | 1 | million gallons (US) | 1
1336.8056
cost | 10 | $/100 cubic feet (ccf) | 1
| cost = | 13368.0556 | [5 empty] | Multiply By…
[6 empty] | million |  | From |  |  | To
[6 empty] | m3 | 1 | Acre-feet | = | 1.2335 | Megalitres (thousand cubic metres)
customer cost
| $/100 cubic feet (ccf) | $/1000 gallons (US) | $/1000 litres
million gallons (US) | 1336.8984 | 1000 | 3786.2355
thousand cubic metres | 353.0944 | 264.1146 | 1000
acre-feet | 435.6 | 325.8288 | 1233.7502
customer cost | 5 | $/1000 gallons (US) | 2
1000
marginal production | 5000 | million gallons (US) | 1
| cost = | 1
>1 = higher customer cost
<1 = lower customer cost
=IF(ISERROR(1/G60),"",(((G24+G25+G40)*G62)+(G37*G61)*INDEX(Sheet1!B2:D4,MATCH(Instructions!G24,Sheet1!A2:A4,0),MATCH('Reporting Worksheet'!I61:J61,Sheet1!B1:D1,0)))/G60)
(reallosses * real loss cost per unit) + (apparent losses * apparent loss cost per unit * unit conversion factor)
=IF(ISBLANK(Instructions!$G$26),"",IF(Instructions!$G$26="Megalitres (thousand cubic metres)",IF(AND(G55>25,G50*20+G51>3000),(((18*G50)+(0.8*G51)+(25*(G51*G53/1000)))*G55/1000000)*365,"Not valid"),IF(AND(G55>40,G50*32+G51>3000),(((5.41*G50)+(0.15*G51)+(7.5*(G51*G53/5280)))*G55)/1000000*365,"Not Valid")))
IF(AND(G55>40,G50*32+G51>3000),(((5.41*G50)+(0.15*G51)+(7.5*(G51*G53/5280)))*G55)/1000000,"Not Valid")))
Logic:
If volume unit is blank show nothing
If instructions is tcm Then
If pressure > 25 AND length of mains * 20 + # connections > 3000 Then
(((18 * length of mains) + (0.8 * # connections) + (25 * (# service connections * avg len of pipe / 1000))) * pressure) /1000
Otherwise not valid
If instructions is gallons Then
If pressure > 40 AND length of mains * 32 + # connections > 3000 Then
(((5.41 * length of mains) + (0.15 * # connections) + (7.5 * (# service connections * avg len of pipe / 5280))) * pressure) /1000000
Otherwise not valid
If instructions is acre-feet Then
If pressure > 40 AND length of mains * 32 + # connections > 3000 Then
(((5.41 * length of mains) + (0.15 * # connections) + (7.5 * (# service connections * avg len of pipe / 5280))) * pressure) /1000000
Otherwise not valid