## Slide 1
UTILITY SOLUTIONS
METER AND AUTOMATION

## Slide 2
Water Meters &
Reading Technology

## Slide 4
Water Meters

## Slide 5
Water Meters
Positive Displacement
Static
Turbine
Compound
Fire Serivce
Hydrant

## Slide 6
Positive Displacement Meter

## Slide 7
Positive Displacement
Mechanical Meter
Meter displaces a certain amount of volume per magnet revolution
Volumetric measurement

## Slide 8
Positive Displacement
Advantages
  Excellent low flow accuracy
  Not affected by upstream flow disturbances
Disadvantages
  Limited in high flow rates by pressure losses
  Limited in size by forces on ball and disc

## Slide 9: Positive Displacement

## Slide 10
T-10 Meter
Applications
  Residential and “light commercial”
  Where small groups of people live and work
Nutating Disc Measuring Chamber
  Sustained long-term accuracy
  Quiet operation: meters in basements
  Allows debris to pass more freely
NSF/ANSI 61, Annexes F & G Approved
  “Green Meter” – manufactured with a lead free alloy

## Slide 11
T-10 Meter
Excellent Low Flow
  1/8 gpm @ 95% accuracy
    AWWA standard is ¼ gpm
  Increased revenue and captured leaks
NSF/ANSI 61 Approved
  Lead free bronze foundry in Tallassee
  Exceeding Safe Drinking Water Regulations since 2001
  First to 100% convert

## Slide 12
T-10 Meter
Strainer for debris
PD Chamber
Different sizes use same chamber technology

## Slide 13
MACH 10 Ultrasonic Meter

## Slide 14
Basic Theory of Operation of Ultrasonic Meters
Flow
Transducer 1
Transducer 2
u

## Slide 15
Basic Theory of Operation of Ultrasonic Meters
Flow
t1
Ultrasonic signal WITH flow

## Slide 16
Basic Theory of Operation of Ultrasonic Meters
Flow
t2
Ultrasonic signal AGAINST flow

## Slide 17
MACH 10 Ultrasonic Meter Technology

## Slide 18
MACH 10 Meter
Neptune developed technology
Extended flow range / extended low flow
Lifetime meter accuracy
Lead free bronze maincase with lifetime warranty
IP68-rated assembly
  Fully potted electronics with tempered glass lens

## Slide 19
Additional Applications
Fire Service Applications
  UL 327B Certification
  Availability: 3/4” – 1”
  Units will be built with RED lid and gasket
Reclaim Water
  Availability: 5/8” – 2”
  Units will be built with LAVENDER lid and gasket

## Slide 20
MACH 10 Solutions – Take Control
Monitoring solutions, which use E-CODER® protocol, include:
  Leak detection
  Reverse flow detection
  Flow indicator
  Empty pipe
  Low battery

## Slide 21
MACH 10 Lifetime Accuracy Performance
Chart: Flow Rate [gpm]
| 0.05 | 0.08 | 0.08 | 0.1 | 0.1 | 20
LSL | 97 | 97 | 98 | 98 | 98.5 | 98.5
USL | 103 | 103 | 102 | 102 | 101.5 | 101.5
Typical | 99.5 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.3

## Slide 22
HP Turbine

## Slide 23
Turbine Technology
Product lines using a turbine:
HP Turbine
TRU/FLO
HP Fire Service Turbine
HP PROTECTUS III
Fire Hydrant Meter
The flow must be conditioned:
No strainer: 8-10 diameters straight pipe upstream
Strainer: 4-6 diameters straight pipe upstream

## Slide 24
What Causes Irregular Flows
Generally, any abrupt change in the plumbing is a potential source of flow irregularities

## Slide 25
HP Turbine
Clean water applications
Cold water measurement
Turbine Rotor is used to measure the velocity
Rotor is magnetically coupled to the register
HP Turbine Features
Hydrodynamically balanced rotor
  Minimizes wear
Calibration vane for small adjustments if needed

## Slide 26
HP Turbines 1 ½” – 10”
Moderate to High Flow Rates
    4-6500 GPM
Accuracy to within +/- 1.5%
    Accuracy calibration vane
Full line is bronze body
    NSF/ANSI 61 approved
    Lead free alloy

## Slide 27
Unitized Measuring Element (UME)
Measuring Element
New Register
Factory Test Ticket

## Slide 28
UME Change Out

## Slide 29
UME Change Out

## Slide 30
TRU/FLO Compound Meter

## Slide 31
TRU/FLO Compound Meter
What is it?
Two meters in one main case
  PD meter for low flow rates
  Turbine for moderate to high flows
Hydraulic Valve
  Transitions flow from PD meter to turbine and vice-versa
HP Turbine Features
  Measures low flows to high flows
  Easy UME change out
  Best turndown available

## Slide 32
TRU/FLO® Compound 2” – 6”x8”
Moderate to High Flow Rates
  1/8-2000 GPM
Hydraulic Valve and Automatic Throttling Valve
  Minimizes crossover range & maximizes revenue
UME, Calibration Vane, & Test Port
  Ease of maintenance and ensures maximum revenue
Full line is bronze body
  NSF/ANSI 61 approved
  Lead free alloy

## Slide 33
TRU/FLO with Strainer
Throttle Tube Door
Turbine Element
Throttle Tube
Calibration Vane
Turbine Register
T-10 Register
Valve Piston
Main Valve

## Slide 34
Low Flow

## Slide 35
Crossover

## Slide 36
Intermediate and High Flow

## Slide 37
Fire Service Meter Line

## Slide 38
Fire Service Product Line
Fire Service HPT
HP PROTECTUS III S
Fire Hydrant

## Slide 39
Fire Service HP Turbine
Fire Service Applications
3” – 10” Sizes
  5 – 6500 GPM
Uses Standard HP Turbine
  UL/FM Listed Basket Strainer
HP Turbine is bronze body
  NSF/ANSI 61 approved
  Lead free alloy

## Slide 40
HP PROTECTUS® III Stainless Steel (S)
Fire Service Applications
NSF/ANSI 61
304 Stainless Steel
20 (10/10) year body warranty
Stainless Steel bolts
304 SS Covers (optional)
4” - 10” sizes / 3/8 to 6500 gpm
UL/FM Listed
Victaulic Coupling
Spring Loaded SS Valve
Automatic Throttle Valve
Test Ports

## Slide 41
UL/FM Approved Strainer

## Slide 42
Utilizes HP Turbine
For medium and high flow through the unit

## Slide 43
HP Protectus III Utilizes T-10
Bypass for low flows

## Slide 44
Knuckle Valve
Knuckle Valve is located behind HP Turbine
Diverts low flow to T-10® side

## Slide 45
Throttle Valve
Throttle Valve is located in the outlet side of the T-10
Protects T-10 from over speed

## Slide 46
Fire Hydrant
3” size
5 to 450 gpm
2” Gate Valve included
Aluminum Construction
No Lead Alloy Cover
NSF 372
Internal Strainer
UME - Factory Calibrated
Accuracy Calibration Vane
Lightweight, easy to handle
Locking register lid

## Slide 47
Moderate to High Flow Rates
Processing Plants
Manufacturing Facilities
Irrigation Lines
Lawn Sprinkler Systems
Wells
Effluent Water in Treatment Plants
Booster (Pump) Stations
Large Batching Operations
Inter-system sales or transfer
Office Buildings
Public Transportation Centers
  WHERE PEOPLE WORK!!

## Slide 48
Low to High Continuous Flow Rates
Apartment Buildings
Motels and hotels
Condominiums
Mobile Home Parks
Hospitals and Schools
Restaurants
Dormitories
Department Stores
Shopping Malls
Public Transportation Centers
  WHERE PEOPLE LIVE!!

## Slide 49
Fire Service Applications
Must be UL/FM Approved
Designated Fire Protection Lines
Any of the HP Turbine or TRU/FLO® meter applications that utilize the same service line to provide fire protection
  WHERE PEOPLE WORK AND LIVE!!

## Slide 50
Important Note on Strainers
Use of strainer strongly recommended!
  Helps correct velocity profile
  Protects turbine from debris

## Slide 51
What Not To Do
51

## Slide 52
Correct Sizing
Historical “Rule of Thumb”:
  Old sizing convention – 3” meter for 3” pipe
Actual Realization:
  Flow capacity not always dictated by pipe size
  More and more customers use low flow devices – e.g. ULF toilets = less consumption
  Building/facilities no longer used for original intentions
    (old processing plant converted to office space)
  Often consultants recommend larger meters due to future growth which never occurs

## Slide 53
AWWA Sizing Guide
Developed in the 1980’s
Collected 5 years worth of data
Corrected sizing in many cases – ex. 2” PD on 6” Pipe
Correct sizing contributes in two major ways:
  Increased annual revenue
  Decreased annual capital expenditures
53

## Slide 54
Reading Systems

## Slide 56: Meter Reading Collection
AMR (automatic meter reading)
  Handheld
  Mobile
AMI (advanced metering infrastructure)
  Fixed Base Radio
  Cellular

## Slide 57
Meter Register

## Slide 58: Meter Register
High Resolution Register
  With meter readings collected every 15 minutes, high resolution readings are key to creating usable consumption profiles.

## Slide 59: Low Resolution (6 digit) Meter Reading

## Slide 60: High Resolution (8 digit) Meter Reading

## Slide 61
Radio Endpoint

## Slide 62
System Technology
Unlicensed, One-Way (900 MHz) Frequency Hopping Spread Spectrum Transmitter
  No FCC license required
  Interference avoidance
  Battery life is dependable
Operational Efficiency
High Output Power – FCC Part 15.247
  Read success rate is typically 99.5%
  Reduces reading time by as much as 40%
No Programming Required
  Ease of Installation and overall reduction in installation cost

## Slide 63
Fixed Network Message Interleaved with Standard Mobile Messages
7 ½ Min
…
…
7 ½ Min
Low Power Mobile Transmission Every 14 Seconds

## Slide 64
1 Watt – Fixed Network Transmission
Patented “3 Readings Packet”
  Flag data
  Current read
  Previous read (-15 minutes)
  12-hour read (- 12 hours)
Hourly data to the host

## Slide 65
AMR
Automatic Meter Reading

## Slide 66
Handheld Meter Reading
Two piece design with Trimble Nomad and Belt Clip Transceiver.
Manual, Touch and Radio Read
Walk by and drive by
Belt Clip Transceiver can be paired with NGO App

## Slide 67
Mobile Meter Reading
Mobile Transceiver paired with laptop
Most efficient mobile reading method optimizing reading distance and processing speed

## Slide 68
NGO App
Available for iOS and Android devices
Bluetooth pairing with Belt Clip Transceiver
RF Test, Data Logging, Off Cycle and Pressure Monitoring

## Slide 69
Data Logging
Ability to download 96 days of hourly readings
Address customer consumption concerns
Graph and report options
Field presentment

## Slide 70
Mobile Meter Reading Software
Provides interface with utility billing system
Route Management
Reporting
Data Logging

## Slide 71
AMI
Advanced Metering Infrastructure - Radio

## Slide 72
Fixed Network AMI
Integrate New Technology Seamlessly
Reduced number of R900® Gateways facilitates AMI Migration
1 Watt Fixed Network transmission
Patented “3 Readings Packet”
  Flag data
  Current read
  Previous read (-15 minutes)
  12-hour read (-12 hours)
  Hourly data to the host

## Slide 73
Migration
Simplify Operations
No programming required for AMI Migration
Fixed Network Message Interleaved with Standard mobile messages

## Slide 74
AMI
Advanced Metering Infrastructure - Cellular

## Slide 75: Cellular System Architecture

## Slide 76: Implementation of Cellular System
Targeted Reading
  Commercial & Industrial
Fixed Base Backfill
  Ability to reach 100% reading without adding collectors
Full Implementation
  Municipal Utility
  Rural Water System

## Slide 77: Benefits of Cellular System
NaaS (network as a service)
  Uses existing cellular network
  Eliminates cost of collectors and maintenance
Large Service Area Coverage
  Ability to reach 100% reading without adding collectors
Full Coverage
  Cellular network allows for complete coverage
Reading Frequency Options

## Slide 78: Reading Frequency Options
Mode | Register Interrogation | Transmit Interval
Basic | 1 Hour | 24 Hours
Advanced | 1 Hour | 4 Hours
Pro | 15 Minutes | 1 Hour

## Slide 79: Installation
Wired to encoded register
Wired to outside mount to maximize cellular coverage
  Will work inside based on cellular coverage
Activate unit
Verify transmission success

## Slide 80
AMI
Head End Software
Meter Data Management Software

## Slide 81
Customer Service
Meter and Maintenance Staff
Finance
Conservation
Utility Management
Your Customers
Meter Data Management Tools For:

## Slide 87
System Health Screen
Collectors Down
Missed Reads
Found Meters
Invalid Readings

## Slide 88
Leaks
Reverse Flow
High Usage
Inactive

## Slide 89
Account View

## Slide 90
Map View
Swipe to toggle
between Account
and Map View

## Slide 91
Customer Portal

## Slide 95
Thank you for
your time.